Electrical Infrared & Thermal Imaging Inspection 2026

Sample Facility (Demo)

123 Example Avenue, Anytown

Report Properties

| Report Title | IR Scan & Electrical Inspection 2026 |
| --- | --- |
| Company Name | Sample Client Inc. |
| Contact Person | Alex Client |
| Phone | (555) 555-0100 |
| Email | contact@example.com |
| Site Name | Sample Facility (Demo) |
| Site Location | 123 Example Avenue, Anytown |
| Thermographer | Joe Smith, Level II Thermographer |
| ITC Certification No. | 123456 |
| Inspection Date | June 01 2026 |

Cover Letter

June 01 2026

Attn: Alex Client

Sample Client Inc.

123 Example Avenue, Anytown

Dear Alex,

Thank you for choosing DTI Suite to complete the electrical infrared inspection at your facility. Enclosed is the full report documenting our findings, including the thermal anomalies detected, their severity, and our recommended corrective actions.

Our certified thermographers inspected the electrical assets listed in the Asset Inventory at the end of this report. Any item flagged for repair should be addressed within the recommended timeframe, and we recommend a follow-up infrared inspection at intervals of no more than twelve months to maintain the reliability of your electrical infrastructure.

Should you have any questions regarding the findings, please do not hesitate to contact us.

Sincerely,

Joe Smith

Level II Thermographer

DTI Suite

Certificate of Infrared Inspection Be it Known That: Sample Client Inc. Has Completed an In-Depth Thermographic Inspection on the Electrical Assets at: Sample Facility (Demo) 123 Example Avenue, Anytown On the Following Date(s): June 01 2026 Scan completed by:; Thermographer:. Joe Smith, Level II Thermographer. Conforming to ASNT SNT-TC-1A, NFPA 70B:23, CSA Z463:24, and NETA MTS (2023).

Table of Contents

| Report Properties | 1 |
| --- | --- |
| Cover Letter | 2 |
| Certificate of Inspection | 3 |
| Table of Contents | 4 |
| IR Report Summary | 5 |
| Findings at a Glance | 6 |
| Severity Matrix | 6 |
| Repair Summary | 6 |
| Year-over-Year Comparison | 7 |
| Temperature Trend by Scan Date | 8 |
| Risk Prioritization | 8 |
| Recommended Re-inspection (NFPA 70B / CSA Z463) | 8 |
| Technician Notes, Observations & Recommendations | 9 |
| Company Summary | 10 |
| Severity Model | 10 |
| What Insurance Companies Require | 10 |
| IR Inspection Sheets | 11 |
| Report Conclusion | 15 |
| Asset Inventory List | 16 |

IR Report Summary

On June 01 2026, DTI Suite conducted a comprehensive thermal inspection of electrical assets at Sample Facility (Demo), located at 123 Example Avenue, Anytown, Canada.

A total of 46 electrical assets were scanned. 2 thermal anomalies were identified in this report. 1 require repair or servicing based on the severity ranking provided. The remainder of anomalies found should be reviewed during the next IR Scan for similarities.

A complete list of all electrical equipment inspected can be found at the end of this report, under the heading “Asset Inventory List”.

To maintain the integrity and reliability of the facility’s electrical infrastructure, DTI Suite recommends conducting follow-up infrared inspections at intervals of no more than twelve months.

Findings at a Glance

46 asset(s) scanned   ·   2 thermal anomaly(ies) flagged   ·   1 require immediate repair

Severity Matrix

Every flagged thermal anomaly is plotted by Severity (thermal condition) against Criticality (importance to operations). Numbered markers are the repair items — their numbers match the Repair Summary below; grey dots are reference-only anomalies logged for monitoring. Items toward the upper-right warrant the most urgent attention.

Repair Summary

| No. | Asset | Label | Location | Max Temp | Problem | Recommendation | Severity | Page |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 16115 | CRAC-1 | Head End | 53.6 °C | Extreme high temperature found. | Shut down equipment immediately. Notify equipment owner. | Repair Immediately | 11 |
| 2 | 246882 | BDFB 401 | Head End | 32.5 °C | High temperature connection. | Un-terminate, clean connection point, re-terminate and torque to manufacturers recommendations. | Potential Problem | 14 |

Numbers match the markers on the Severity Matrix. In the digital report, click an asset number or page to jump to that asset's inspection sheet.

Year-over-Year Comparison

Compared with 2025, across assets scanned in both years: 1 worsened, 2 improved, 0 unchanged  ·  1 new asset(s) in 2026.

Assets to watch — severity (rated 1–10, higher = worse) increased since last year:

| Asset Number | Location | Equipment | Severity 2025 | Severity 2026 | Change |
| --- | --- | --- | --- | --- | --- |
| 246882 | Head End | BDFB 401 | 4 | 8 | +4 |

Assets (click to view): #246882    #16115

Each line is one asset's severity across the inspection program; the haloed point is this year's reading. Assets at repair-level severity are shown even when unchanged; a single dot is a new asset first recorded this year. The chart extends as future scans are completed.

Temperature Trend by Scan Date

Each line is one asset's maximum measured temperature across inspections at this site — rising lines are developing problems, flat lines are healthy connections.

Risk Prioritization

| Condition | Findings | Industry failure likelihood |
| --- | --- | --- |
| Repair Immediately | 1 | ≈95% fail within 30 days (ΔT > 20 °C) |
| Potential Problem | 1 | ≈25% fail within the next 2 to 5 years |

Failure likelihoods are indicative, based on published NETA / industry temperature-rise practice; actual risk varies with load, duty cycle and environment.

Recommended Re-inspection (NFPA 70B / CSA Z463)

Based on the anomalies identified, a follow-up infrared inspection is recommended within 12 months (next due 2027-06-01). Equipment flagged for immediate or required repair should be re-checked once the corrective work is done.

📅  Schedule the re-inspection:  Add to Google Calendar    ·    Download calendar file (.ics)

The .ics file (saved beside this report) opens your default calendar — Apple Calendar, Windows Calendar or Outlook; the Google link opens in your browser. The event repeats annually with a two-week reminder.

Re-inspection intervals follow a condition-based maintenance schedule consistent with NFPA 70B (US) and CSA Z463 (Canada). Neither standard prescribes fixed thermographic re-scan intervals; the intervals here are driven by each finding's condition, and assets in normal condition follow the facility's routine cycle (typically 1–5 years). Next-due dates are calculated from the inspection date.

Technician Notes, Observations & Recommendations

- All areas are very clean with access to all electrical equipment. All electrical equipment is in excellent condition.

- IR Scan could not be performed on any of the feeder breakers in the main switchboard due to breakers having a dead front and the back of the switchboard being inaccessible. It is recommend to isolate the switch board and performing mechanical and electrical maintenance on the switchboard as ANSI/NFPA 70B state that electrical equipment  including Panelboard, Switchboards should be cleaned and mechanically/electrically tested every 5 years. NFPA 70B also states that if equipment has missed their last two maintenance cycles they should be tested within 12 months.

- Arc Flash study is older than 5 years. CSA Z462 and NFPA 70E state that Arc flash studies should be reviewed periodically, such as every five years, or when changes are made to the electrical system. Recommend updating Arc Flash study and labels to comply with CSA Z462.

Company Summary

DTI Suite provides infrared thermographic inspection of electrical systems.

The purpose of an infrared inspection is to detect abnormal heat in energized electrical equipment. Unusual heating is commonly caused by loose or un-torqued connections, oxidation between dissimilar metals, circuit overloading, load imbalance, or harmonics.

This survey acts as a predictive tool to detect unforeseen problems in electrical distribution systems and to satisfy insurance requirements for an infrared scanning program per current industry guidelines.

Per NFPA 70B 7.4.4, single-point thermal measurements should be taken at a minimum of 40% of nominal circuit loading after reaching steady-state temperature. Readings under minimal load can falsely indicate a “No-Fault” condition.

Severity Model

| Rating | ΔT vs Similar Component | ΔT vs Ambient Air | Recommended Action |
| --- | --- | --- | --- |
| Reference Only | 1 – 5 °C | 1 – 10 °C | Reference only; review at next scheduled scan. |
| Potential Problem | 5 – 10 °C | 11 – 20 °C | Possible deficiency; warrants investigation. |
| Repair Required | 10 – 20 °C | 21 – 40 °C | Probable deficiency; repair as time permits. |
| Repair Immediately | > 20 °C | > 40 °C | Major discrepancy; repair immediately. |

What Insurance Companies Require

This inspection is documented to meet the requirements commonly specified by insurers and authorities having jurisdiction (AHJ):

| Requirement | Included |
| --- | --- |
| Level II Thermographer certification | ✓ |
| Minimum 640 × 480 infrared image resolution | ✓ |
| Complete asset list of all equipment scanned | ✓ |
| Traffic-light severity rating (green / yellow / red) | ✓ |
| Thermal analysis with measured temperatures | ✓ |
| Technician notes, observations and comments | ✓ |
| Prioritized repair recommendations | ✓ |

| Asset Tag No. |  | 16115 |  |  | Equipment Label: |  | CRAC-1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fault Rating: |  | Repair Immediately |  |  |  |  |  |  |
| Image Title: | DTI_00317.jpg |  | Image Date: |  |  | Camera Make & Model: |  | HIKMICRO |

| Radiometric Image | Digital Image |
| --- | --- |

| Measurements: |  |
| --- | --- |
| Sp1 | 53.6 °C |
| Sp2 |  |
| Bx MAX | 53.6 °C |
| Δt | 36.6 °C |

| Parameters: |  |
| --- | --- |
| Emissivity | 0.97 |
| Distance | 0.00 m |
| Atmospheric temp. | 21.2 °C |
| Relative humidity | 50% |
| Reference temp. | 21.2 °C |
| Ext. optics temp. | 0.0 °C |
| Ext. optics trans. | 1.00 |
| Lens |  |

| Equipment Summary: |  |
| --- | --- |
| Asset Tag No. | 16115 |
| Location: | Head End |
| Label: | CRAC-1 |
| Equipment Type: | Control Panel |
| Rating: | 208V, 107.5A |
| Problem: | Extreme high temperature found. |
| Recommendation: | Shut down equipment immediately. Notify equipment owner. |
| Action: | Repair Immediately |

| Amperage Readings: |  |  |
| --- | --- | --- |
|  | Rated | Recorded |
| Phase A | 107.5A | 16.5A |
| Phase B | 107.5A | 16.5A |
| Phase C | 107.5A | 16.5A |

Technician Notes:

IR Scan is showing a high resistance connection on the Phase A, load side stak-on crimp connection for the main fan contactor. The current draw is balanced and the highest temperature is on the stak-on crimp indicating a failing crimp connection. Recommend replacing stak-on crimp. Current Draw: Phase A: 16.5A, B: 16.5A, C: 16.5A

| Asset Tag No. |  | 246861 |  |  | Equipment Label: |  | Distribution Section Feeders To Dist. Panels RDP-1… |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fault Rating: |  | Reference Only |  |  |  |  |  |  |
| Image Title: | FLIR3307.jpg |  | Image Date: | 2026-06-01 14:18:11 |  | Camera Make & Model: |  | FLIR T865 |

| Radiometric Image | Digital Image |
| --- | --- |

| Measurements: |  |
| --- | --- |
| Sp1 | 24.8 °C |
| Sp2 |  |
| Bx MAX | 26.1 °C |
| Δt | 1.3 °C |

| Parameters: |  |
| --- | --- |
| Emissivity | 0.98 |
| Distance | 0.97 m |
| Atmospheric temp. | 20.0 °C |
| Relative humidity | 50% |
| Reference temp. | 20.0 °C |
| Ext. optics temp. | 19.0 °C |
| Ext. optics trans. | 1.00 |
| Lens | FOL10 |

| Equipment Summary: |  |
| --- | --- |
| Asset Tag No. | 246861 |
| Location: | Main Electrical Room |
| Label: | Distribution Section Feeders To Dist. Panels RDP-1 & RDP-2 |
| Equipment Type: | Main Switchboard Distribution Section |
| Rating: | 120/208V, 3000A |
| Problem: | No significant thermal irregularities. |
| Recommendation: | IR Ok. Monitor condition. |
| Action: | Monitor |

| Amperage Readings: |  |  |
| --- | --- | --- |
|  | Rated | Recorded |
| Phase A | 3000A | 206A |
| Phase B | 3000A | 200A |
| Phase C | 3000A | 195A |

Technician Notes:

IR Ok, temperature corelates to the current draw. Photo is for reference only. Feeder Dist. RDP-1: Current Draw: Phase A: 206A, B: 200A, C: 195A Feeder Dist. RDP-2: Current Draw: Phase A: 205A, B: 201A, C: 200A

| Asset Tag No. |  | 246871 |  |  | Equipment Label: |  | Panel RP1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fault Rating: |  | Reference Only |  |  |  |  |  |  |
| Image Title: | FLIR3309.jpg |  | Image Date: | 2026-06-01 14:30:52 |  | Camera Make & Model: |  | FLIR T865 |

| Radiometric Image | Digital Image |
| --- | --- |

| Measurements: |  |
| --- | --- |
| Sp1 | 23.1 °C |
| Sp2 |  |
| Bx MAX | 25.7 °C |
| Δt | 2.7 °C |

| Parameters: |  |
| --- | --- |
| Emissivity | 0.98 |
| Distance | 0.48 m |
| Atmospheric temp. | 20.0 °C |
| Relative humidity | 50% |
| Reference temp. | 20.0 °C |
| Ext. optics temp. | 19.0 °C |
| Ext. optics trans. | 1.00 |
| Lens | FOL10 |

| Equipment Summary: |  |
| --- | --- |
| Asset Tag No. | 246871 |
| Location: | Battery Room |
| Label: | Panel RP1 |
| Equipment Type: | Electrical Panel |
| Rating: | 120/208V, 225A |
| Problem: | Suspected loose connection. |
| Recommendation: | Replace breaker. |
| Action: | Repair Required |

| Amperage Readings: |  |  |
| --- | --- | --- |
|  | Rated | Recorded |
| Phase A | 225A | 11A |
| Phase B | 225A | 11A |
| Phase C | 225A | 11A |

Technician Notes:

IR Scan is showing a high resistance connection on the line side screw of the 20A breaker for CCT 3: Hub room lights. Technician checked screw last year which is stripped and un able to be tightened. *Screw has been replaced. Re scan has been performed and no thermal anomaly was detected. No further repair required, will review next IR Scan. Current Draw: 11A

| Asset Tag No. |  | 246882 |  |  | Equipment Label: |  | BDFB 401 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Fault Rating: |  | Potential Problem |  |  |  |  |  |  |
| Image Title: | FLIR3311.jpg |  | Image Date: | 2026-06-01 14:57:01 |  | Camera Make & Model: |  | FLIR T865 |

| Radiometric Image | Digital Image |
| --- | --- |

| Measurements: |  |
| --- | --- |
| Sp1 | 26.2 °C |
| Sp2 |  |
| Bx MAX | 32.5 °C |
| Δt | 6.3 °C |

| Parameters: |  |
| --- | --- |
| Emissivity | 0.98 |
| Distance | 0.28 m |
| Atmospheric temp. | 20.0 °C |
| Relative humidity | 50% |
| Reference temp. | 20.0 °C |
| Ext. optics temp. | 19.0 °C |
| Ext. optics trans. | 1.00 |
| Lens | FOL10 |

| Equipment Summary: |  |
| --- | --- |
| Asset Tag No. | 246882 |
| Location: | Head End |
| Label: | BDFB 401 |
| Equipment Type: | DC Panel |
| Rating: | 48VDC, 800A |
| Problem: | High temperature connection. |
| Recommendation: | Un-terminate, clean connection point, re-terminate and torque to manufacturers recommendations. |
| Action: | Repair Required |

| Amperage Readings: |  |  |
| --- | --- | --- |
|  | Rated | Recorded |
| Phase A | 800A |  |
| Phase B | 800A |  |
| Phase C | 800A |  |

Technician Notes:

IR Scan is showing a higher than normal temperature on the wire labeled 507-49/B1/-48V where it connects to -48 Bus B1. The temperature on this connection is significantly higher than any other scanned at this Hub. Due to the highest temperature being at the termination point it is recommend to check connections. *Lug has been replaced and relocated to new bus. Re scan performed and no thermal anomaly was detected. No further repair required, will review next IR Scan.

Report Conclusion

The thermal anomalies identified in this report should be addressed according to the urgency and recommended timeframes provided. Any anomalies labeled “Repair Immediately” should be re-evaluated through a follow-up infrared scan after repair or replacement, with all other items requiring a follow-up IR scan within 12 months of the original inspection date.

Given the essential nature of the electrical equipment scanned, it is strongly recommended that the facility implement routine electrical infrared inspections at intervals not exceeding 12 months.

We appreciate the opportunity to support your team and thank you for choosing DTI Suite.

This report has been approved by:

,

DTI Suite

Asset Inventory List

| Asset No. | Room / Location | Equipment Label | Equipment | Make | Model | Rating (V, A) | IR Photo | Comments | Severity | Criticality | Page |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 246855 | Main Electrical Room | Main Breaker | Breaker | Square D | NW32H1 | 208V, 3200A |  | IR Ok |  |  |  |
| 246856 | Main Electrical Room | Generator Breaker | Breaker | Square D | RG2000 | 208V, 2000A |  | IR Ok |  |  |  |
| 246857 | Main Electrical Room | Tap Box | Breaker | Square D | RG2000 | 208V, 2000A |  | IR Ok |  |  |  |
| 246858 | Main Electrical Room | 800A Fusible Disc. Switch | Breaker | Square D | MHL36800 | 208V, 800A |  | IR Ok |  |  |  |
| 246859 | Main Electrical Room | Feeder To ATS | Breaker | Square D | NW32H | 208V, 3200A |  | IR Ok |  |  |  |
| 246860 | Main Electrical Room | ATS | ATS | ASCO | G7ADTBB330005XC | 120/208V, 3000A |  | IR Ok |  |  |  |
| 246861 | Main Electrical Room | Distribution Section Feeders To Dist. Panels RDP-1 & RDP-2 | Main Switchboard Distribution Section | CSL | JB14718 | 120/208V, 3000A | FLIR3307 | IR Ok, temperature corelates to the current draw. Photo is for reference only. Feeder Dist. RDP-1: Current Draw: Phase A: 206A, B: 200A, C: 195A Feeder Dist. RDP-2: Current Draw: Phase A: 205A, B: 201A, C: 200A | 2 | 8 | 12 |
| 246861 | Main Electrical Room | Distribution Section - Feeder To RP-1 | Main Switchboard Distribution Section | CSL | JB14718 | 120/208V, 3000A |  | IR Scan is showing a higher temperature on the Phase B of the breaker. Temperature corelates to the current draw which is highest on Phase B. No repair required, photo is for reference only. Current Draw: Phase A: 21A, B: 54A, C: 42A |  |  | 12 |
| 246862 | Main Electrical Room | Surge Protector | Control Panel | Surgelogic | TVS2EMA48AIC | 120/208V, 30A |  | IR Ok |  |  |  |
| 246863 | Main Electrical Room | Panel M2 | Distribution Panel | Square D | HCP | 120/208V, 400A |  | IR Ok |  |  |  |
| 246864 | Main Electrical Room | Panel M1 | Distribution Panel | Square D | HCP | 120/208V, 400A |  | IR Ok |  |  |  |
| 246865 | Main Electrical Room | Panel M3 | Distribution Panel | Square D | HCP | 120/208V, 400A |  | IR Ok |  |  |  |
| 246866 | Battery Room | INV-DP | Distribution Panel | Square D | HCP | 120/208V, 400A |  | IR Ok |  |  |  |
| 246867 | Battery Room | INV. 1 | Inverter | Benning | Invertronic-M 120KVA | 120.208V, 347A |  | IR Ok |  |  |  |
| 246867 | Battery Room | INV. 2 | Inverter | Benning | Invertronic-M 120KVA | 120.208V, 347A |  | IR Ok |  |  |  |
| 246868 | Battery Room | Rectifier Bay | Rectifier | Argus | 053-162-20 | 48VDC, 2200A |  | IR Ok |  |  |  |
| 246868 | Battery Room | Rectifier Bay | Rectifier | Argus | 053-162-20 | 48VDC, 2200A |  | IR Ok |  |  |  |
| 246868 | Battery Room | Distribution Bay | Distribution Panel | Argus | 053-162-20 | 48VDC, 3600A |  | IR Ok |  |  |  |
| 246868 | Battery Room | Distribution Bay | Distribution Panel | Argus | 053-162-20 | 48VDC, 3600A |  | IR Ok |  |  |  |
| 246868 | Battery Room | Distribution Bay | Distribution Panel | Argus | 053-162-20 | 48VDC, 3600A |  | IR Ok |  |  |  |
| 246869 | Battery Room | Panel RDP-2 | Distribution Panel | Square D | HCM | 120/208V, 800A |  | IR Ok |  |  |  |
| 246870 | Battery Room | Panel RDP-1 | Distribution Panel | Square D | HCM | 120/208V, 800A |  | IR Ok |  |  |  |
| 246871 | Battery Room | Panel RP1 | Electrical Panel | Square D | NF | 120/208V, 225A | FLIR3309 | IR Scan is showing a high resistance connection on the line side screw of the 20A breaker for CCT 3: Hub room lights. Technician checked screw last year which is stripped and un able to be tightened. *Screw has been replaced. Re scan has been performed and no thermal anomaly was detected. No further repair required, will review next IR Scan. Current Draw: 11A | 2 | 5 | 13 |
| 246872 | Battery Room | Battery Bank 1 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246873 | Battery Room | Battery Bank 2 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246874 | Battery Room | Battery Bank 3 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246875 | Battery Room | Battery Bank 4 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246876 | Battery Room | Battery Bank 5 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246877 | Battery Room | Battery Bank 6 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246878 | Battery Room | Battery Bank 7 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246879 | Battery Room | Battery Bank 8 | Breaker | Electric Equipment Engineering | EEJS400 | 80VDC, 1200A |  | IR Ok |  |  |  |
| 246880 | Head End | INVP-B | Electrical Panel | Square D | NQ | 120/208V, 225A |  | IR Ok |  |  |  |
| 246881 | Head End | BDFB 201 | DC Panel | Argus | 053-163-20 | 48VDC, 800A |  | IR Ok |  |  |  |
| 246882 | Head End | BDFB 401 | DC Panel | Argus | 053-163-20 | 48VDC, 800A | FLIR3311 | IR Scan is showing a higher than normal temperature on the wire labeled 507-49/B1/-48V where it connects to -48 Bus B1. The temperature on this connection is significantly higher than any other scanned at this Hub. Due to the highest temperature being at the termination point it is recommend to check connections. *Lug has been replaced and relocated to new bus. Re scan performed and no thermal anomaly was detected. No further repair required, will review next IR Scan. | 8 | 7 | 14 |
| 246883 | Head End | BDFB 601 | DC Panel | Argus | 053-163-20 | 48VDC, 800A |  | IR Ok |  |  |  |
| 246884 | Head End | BDFB 608 | DC Panel | Alpha | 914 | 48VDC, 640A |  | IR Ok |  |  |  |
| 246885 | Head End | BDFB 801 | DC Panel | Argus | 053-163-20 | 48VDC, 800A |  | IR Ok |  |  |  |
| 246886 | Head End | BDFB 906 | DC Panel | Alpha | 914 | 48VDC, 640A |  | IR Ok |  |  |  |
| 246887 | Head End | BDFB 1001 | DC Panel | Argus | 053-163-20 | 48VDC, 800A |  | IR Ok |  |  |  |
| 246888 | Head End | BDFB 1201 | DC Panel | Argus | 053-163-20 | 48VDC, 800A |  | IR Ok |  |  |  |
| 246889 | Head End | INVP-A | Electrical Panel | Square D | NQ | 120/208V, 225A |  | IR Ok |  |  |  |
| 16115 | Head End | CRAC-1 | Control Panel | Liebert | DS053AUC0EI664A | 208V, 107.5A | DTI_00317 | IR Scan is showing a high resistance connection on the Phase A, load side stak-on crimp connection for the main fan contactor. The current draw is balanced and the highest temperature is on the stak-on crimp indicating a failing crimp connection. Recommend replacing stak-on crimp. Current Draw: Phase A: 16.5A, B: 16.5A, C: 16.5A | 7 | 7 | 11 |
| 16116 | Head End | CRAC-3 | Control Panel | Liebert | DS053AUC0EI664A | 208V, 107.5A |  | IR Ok |  |  |  |
| 16117 | Head End | CRAC-2 | Control Panel | Liebert | DS053AUC0EI664A | 208V, 107.5A |  | IR Ok |  |  |  |
| 16118 | Head End | CRAC-4 | Control Panel | Liebert | DS053AUC0EI664A | 208V, 107.5A |  | IR Ok |  |  |  |
| 16119 | Head End | CRAC-5 | Control Panel | Liebert | DA085DP1CD585S | 208V, 152.2A |  | IR Ok |  |  |  |